## A.C.
PROJECT - BILL OF QUANTITIES FOR AIR-CONDITIONING WORKS (GROUND FLOOR).
BANK - UCO BANK
BRANCH & ATM - CHARBAGH
REGION - LUCKNOW
Note : For any make, if OEM doesn’t has specific star rating for the product but that product has equivalent energy saving as compared to the star rating, then vendor shall mentioned the same against the model number.
Sr. No | SPLIT TYPE AIR CONDITIONERS
A. | PART -A
HIGH SIDE WORK
| Description | Unit | Quantity | Rate | Amount
1 | Supplying, erection, testing and commissioning following wall mounted Split/ Roof mounted cassette units of (Toshiba/ Mitsubhishi/ Hitachi/ Daikin/LG/Bluestar/ Carrier/ Voltas) with cordless remote complete with all necessary fittings duly insulated with 9 mm thick nitrile rubber pipe insulation with (evaporator coil – copper only), fan and fan motor, machine control panel improved Refrigerant Joints, .Air conditioners shall be fitted with hermetically sealed type suction cooled reciprocating or discharge cooled rotary compressor or scroll compressor. Compressor unit operating on R-22/ R-410. All complete as per drawing, approval and instructions of the Employer (Rates to be inclusive of Copper refrigerant pipe with insulation and Drain pipe up to 5 Mtr. length).
a | 1.0 TR wall mounted split unit (Minimum 5-Star rating inverter type) including all necessary fittings and mountings as specified by the manufacturer. | Nos. | 1
b | 1.5 TR wall mounted split unit (Minimum 5-Star rating inverter type) including all necessary fittings and mountings as specified by the manufacturer. | Nos. | 1
c | 2.0 TR wall mounted split unit (Minimum 5-Star rating inverter type) including all necessary fittings and mountings as specified by the manufacturer. | Nos. | 0
PART A – HIGH SIDE WORK SUB TOTAL AMOUNT
Add - Goods & Services Tax (CGST) (Rs.)
Add - Goods & Services Tax (SGST) (Rs.)
Add - Transportation / Cartage (Rs.)
TOTAL OF PART-A
1 | EXTRA REFRIGERANT PIPING
Supplying and laying of Extra copper refrigerant piping with nitrile rubber pipe insulation, both of size as specified by the manufacturer suitable for 1.0 TR/ 1.5/2.0 TR Split type AC and 2.0/3.0 TR Cassette AC (From Indoor to outdoor Units) Beyond 3 M.
a | For 1.0 / 1.5 / 2.0 TR Split unit | Mtr. | 60
b | For 2.0/3.0 TR Cassette AC | Mtr. | 0
2 | DRAIN PIPING
Providing and fixing drain piping up to drain as directed by the engineer in charge with all accessories e.g. elbows, unions, sockets, reducers, reducing tees, nipples etc. Complete job including cutting chiseling in walls, fixing with GI clamps,floor and making good of all chases/ cuts etc. and discharging the drain into a floor trap/ gully as per site conditions with insulation, both as specified by the manufacturer.
a | 25 mm dia PVC drain pipe for Split AC | Mtr. | 55
3 | AUTOMATIC VOLTAGE CONTROLLER
Stabilizer shall be Automatic version with copper coil transformer and the voltage selection range shall be minimum depending on lowest peak recorded average in a month. Precise output voltage range (130V-170V to 240V -270 V). Ensure the rating of Stabilizer shall be in accordance with max rated power of ACs considering instantaneous peak load fluctuation.
Providing and fixing Stabilizer with 3-4 step relay and input voltage range of 130-270 V and output to be 230- 240 V (Blue bird/ Logic state/ Inline/ V-Gaurd/Equivalent Reputed Make) (copper winding).
a | 3 KVA (For 1.0 TR Split AC) | Nos. | 0
b | 4 KVA (For 1.5 TR Split AC) | Nos. | 3
c | 5 KVA (For 2.0 TR Split AC) | Nos. | 0
4 | AIR-CONDITIONERS STAND
MS-STAND - Providing and fixing of lockable caging for outdoor unit grouted on wall or on roof with open able shutter made of 10 X 10 mm MS square bars placed vertically @ 5” c/c welded with 40 X 3 mm MS flat all- round. The frame shall be of angle 35mm*35mm and it shall be fixed to wall or roof with proper MS bracket to tackle the weight of outdoor unit. Item includes all necessary hardware, priming coat, synthetic enamel paint, hanger, clamps other accessories etc. All complete as per approval and instructions of the employer. Size shall be adequate for AC outdoor size & sufficient space around the outdoor suitable for servicing purpose for Outdoor unit.
a | For 1.0 / 1.5 TR Hi Wall split units | Nos. | 3
b | For 2.0TR Hi Wall split units | Nos. | 0
5 | ELECTRICAL CABLES
Suitable IS/BIS standard Cable of 1.1-2.2 KV, Multi strand, FRLS 2- 4 C / 1.5/2.5 -6.0 Sqmm) as per design requirement of Peak load calculation of specific ACs system installed at site with 1”/1/2"/2” PVC conduit pipe between indoor/outdoor unit
a | Supplying and laying of Extra Electrical interconnecting control cable from indoor to outdoor of size as specified by the manufacturer suitable for 1.0 TR/ 1.5/2.0 TR Split type AC. | Mtr. | 65
6 | TIMER
a | Supplying, installation and commissioning of automatic 24 HRS. programmable TIMER of required capacity to run A.C. alternately (MDS/ L&T/ Other reputed make). | Nos. | 0
7 | CORE CUTTING
a | Core cutting member in Non RCC | Nos. | 3
PART B –LOW SIDE WORK SUB TOTAL AMOUNT
Add - Goods & Services Tax (CGST) (Rs.)
Add - Goods & Services Tax (SGST) (Rs.)
Add - Transportation / Cartage (Rs.)
PART B – LOW SIDE WORK SUB TOTAL AMOUNT
GRAND TOTAL (PART A + PART B) INCLUDING GST