## Estimate (Branch)
SCHEDULE FOR THE PROPOSED ELECTRICAL WORK TO BE PROVIDED AT THE UCO BANK, ATM, DHORAJI.
Sr. No. | Item Description | Qty. | Rate | Unit | Amount
NOTE : ALL CHAIRS OR CHASES IN WALLS / COLUMNS / SLABS MADE BY THE ELECTRICAL CONTRACTOR FOR INSTALLATION OF CONDUITS / S.B. / BOXES ETC. THE FILLING OF THE SAME IS IN THE SCOPE OF THE ELECTRICAL CONTRACTOR INCLUDING ALL NECESSITY MATERIAL AND LABOUR.
A | INTERNAL WIRING:
1 | P and M point wiring in concealed in walls, furniture's & for above false ceiling, or on ceiling, on beams shall be fixed with saddles & spacers etc., with conduits taken in slab with 20 mm dia PVC Rigid conduits 1.5 mm thick ISI mark with 2 nos. of 1.5 sq. mm. & 1 nos. of 1 sq. mm. with modular switch with company made flush metal box/surface PVC box etc. comp. with nec. main lines for switch board from DB of mains of 2 nos. of 2.5 sq.mm wire and 1 no.of 1.0 sqmm pvc Insulated copper conductor wire laying in with 20 mm/25 mm dia PVC rigid conduits 1.5 mm thick ISI mark .These will be used with point wiring of light, fan, ex. fan, call bell points, etc { Max. 3 Switchboards in one circuit - One Sp MCB }.
a) | One 5A switch controlling one light/fan point | 2 |  | Nos
b) | One switch controlling Two light points | 2 |  | Nos
c) | 5A socket outlet with 5A switch ( on common board) | 5 |  | Nos
2 | SITC of 6/16 Amp. Switch and socket complete with necessary require wiring from PDB of 2 no of 4.0 sqmm wires and 1 no of 2.5 sqmm PVC Insulated copper conductor wire laying in with 20 mm/25 mm dia PVC rigid conduits 1.5 mm thick ISI mark. These will be used with point wiring of power points, etc. | 4 |  | Nos.
3 | Sign board point with 2 x 4.00 sq.mm + 1 x 1.5 sqmm earth wire circuit from main panel to sing board at entrance with suitable junction box and 3 point connector. | 1 |  | Nos.
4 | SITC of 20 A / 25 A , 230 V, with DP MCB all enclosed in a prefabricated M S boxes complete to the satisfaction of E.I.C. For SPLIT AC - CASSETTE AC 1.0 TR / 1.5TR / 2.0 TR unit with necessary require wiring from ACDB of 2 no of 4.0 sqmm wires and 1 no of 2.5 sqmm PVC Insulated copper conductor wire laying in with 20 mm/25 mm dia PVC rigid conduits 1.5 mm thick ISI mark. These will be used with point wiring of A.C. points ,etc . [This point should be installed near Split / window AC in concealed manner.] The height of switchboard must be at reachable point for easily operation. - from that point to Split AC , empty conduit + necessary bends must in concealed mode by ele. contractor. | 2 |  | Nos.
B | SITC OF LIGHT/FAN FIXTURES:
Supply & Installation, testing and commissioning (including supply and fixing flexible wires from holder to fixtures hardwares etc.) of…. - The LED / PL / TUBE lamps should be of same make as fixture make. - The marking & cutting of fixtures should be in ele. contractor's scope.. fixtures should be approved by bank's ele. engineer / ele. consultant / architect. from the given make list before installations. LM 79 & LM 80 test reports to be submited. nichia LED / cree LED should be used by manufacture.
1 | LED 1 x 36 W ( 3000 lumens ) ( 2' X 2') RECESS MOUNTED LUMINAIRE with making earthing conection complete to be recessed in false ceiling with all necessary hardwares, hanging - die cast frame arrangement, chains, hook etc. complete. | 1 |  | Nos.
2 | 1 x 9/10 W SQUARE/ROUND LED DOWN LIGHTER to be recessed in false ceiling with all necessary hardwares, chains, hook etc. complete. | 4 |  | Nos.
C | COMPUTER POWER SUPPLY SYSTEM:
1 | SITC of 2 nos. of 6 A, 5 pin Sockets and 1 no. of 6\16 A socket below table outlets with one 16 A switches Computer power supply with concealed company made metallic boxes or PVC flush box on walls / furniture's / trunking etc complete all respect with necessory wiring of mains of 2 no of 2.5 sq mm and 1 no of 1.5 sqmm pvc insulated copper conductor multi-stranded flexible wire with 20/25 dia. PVC conduits with accessories duly burried under floor with necessary chasing / breaking in floor and to be refinished with all necessary civil material etc. complete from DB to Computer power supply boards.{Maxi. 3 computers in one circuit}. complete with necessary termination etc. complete. LOOP POINTS MUST BE OF SAME SIZED WIRES. | 2 |  | Nos
2 | S & I of 2 nos. of 6 A, 5 pin Sockets and 1 no. of with one 6 A switches row power supply with concealed company made metallic boxes or PVC flush box on walls / furniture's / trunking etc complete all respect with necessory wiring of mains of 2 no of 2.5 sq mm and 1 no of 1.5 sqmm pvc insulated copper conductor multi-stranded flexible wire with 20/25 dia. PVC conduits with accessories duly burried under floor with necessary chasing / breaking in floor and to be refinished with all necessary civil material etc. complete from DB to Computer power supply boards.{Maxi. 3 Raw Power Points in one circuit}. complete with necessary termination etc. complete. LOOP POINTS MUST BE OF SAME SIZED WIRES. | 2 |  | Nos
D | DISTRIBUTION BOARD AND PANELS:
1 | SITC of metalic double door type distribution board with all necessary connection complete to be installed concealed in wall / surface mount complete. The DB should be of same make as MCB.
a) | UPS 6 WAY SPN DB (for ATM) | 1 |  | Nos
incoming : 32 A DP MCB - 1 No. for UPS Incoming
Outgoing : 25 A DP MCB - 1 No. + 10A SP - 2 No. for UPS Outgoing
b) | 12 - WAY SPN DB: (ATM DB) | 1 |  | Nos
incoming : 32A FP MCB-1 No.
outgoing : 25 A DP MCB (1nos) + 10/20A SP MCB (2 nos)
20A AC Cyclic Timer for AC - 1 No..
E | EARTHING SYSTEM:
1 | Supply, laying and jointing of following wire / strip / earth cable on walls, ceiling etc. With necessary non rusting clamps, washers, nuts and bolts etc complete
a) | 8 SWG CU. Wire with 20 mm dia. PVC rigid conduit duly cleated / concealed / burried in floor etc. complete (Connect From Branch Earthing) | 40 |  | Rmt
F | CABLE & CABLE TERMINATIONS:
1 | SITC of following sizes of PVC insulated PVC sheathed copper / aluminum conductor armoured cable to be laying in existing cable trench or to be laid in existing pipes of with necessary clamps, spacers with cleating on wall ceiling etc. complette to the satisfaction of EIC, (LENGTH TO BE VERIFY AT SITE) including supply and fixing of brass single compression type cable glands and crimping type aluminum / copper lugs suitable for terminations of armoured cables of following overall diameters, incl.
a) | 3.5 x 35 sq. mm. Alu. Conductor AYFY cable. (main cable-Main Panel to Main SFU ) | 8 |  | Mtr.
b) | 4 x 4 sq. mm. Cu. Conductor YWY cable. (Main Panel to Input UPS/ATM DB) | 25 |  | Mtr.
c) | 16 sq. mm. single core wire supply & laying in flexible pipe for main load wire from meter to main switch | 12 |  | Mtr.
d) | 3 C X 4.0 sq. mm flexible Cu. cable with 20 mm/25 mm dia PVC rigid conduits 1.5 mm thick ISI mark . ( UPS to UPS O/P DB & UPS I/P DB to UPS). | 10 |  | Mtr.
G | DATA/STRUCTURED CABLING:
1 | SITC of CAT 6, RJ 45 information outlet (I/O) of D-link make with front modular cover plate, flush box metallic or PVC for trucking system with terminations etc complete. SITC of CAT 6 UTP pvc insulated copper conductor data cable of D-Link make with 20/25 dia. PVC conduit with accessories duly burried under floor with necessary chasing/breaking in floor and to be regishide with all necessary civil material etc. or to be cleated on wall/ceiling witth saddles/spacer etc. necessary termination etc. with ferrule numbering at both ends of each of piece of cable etc. comp. | 3 |  | Nos
2 | Supply and crimping of RJ 45 connector with proper testing | 3 |  | Nos
3 | Supply & Fixing the Patch cord 2Mtr. Long (Factory built) When supplying, then first ask to BM/Consultant/Architect/Bank Authority. | 3 |  | Nos
4 | Supply & Fixing the Patch cord 1Mtr. Long (Factory built) When supplying, then first ask to BM/Consultant/Architect/Bank Authority. | 3 |  | Nos
Total Rs.
Sign & Seal of the Contractor

## Estimate (ATM)
COST ESTIMATES FOR THE PROPOSED ELECTRICAL WORK TO BE PROVIDED AT THE UCO BANK, DHORAJI (ATM), DHORAJI.
Sr. No. | Item Description | Qty. | Rate | Unit | Amount
NOTE : ALL CHAIRS OR CHASES IN WALLS / COLUMNS / SLABS MADE BY THE ELECTRICAL CONTRACTOR FOR INSTALLATION OF CONDUITS / S.B. / BOXES ETC. THE FILLING OF THE SAME IS IN THE SCOPE OF THE ELECTRICAL CONTRACTOR INCLUDING ALL NECESSITY MATERIAL AND LABOUR.
A | INTERNAL WIRING:
1 | P and M point wiring in concealed in walls, furniture's & for above false ceiling, or on ceiling, on beams shall be fixed with saddles & spacers etc., with conduits taken in slab with 20 mm dia PVC Rigid conduits 1.5 mm thick ISI mark with 2 nos. of 1.5 sq. mm. & 1 nos. of 1 sq. mm. with modular switch with company made flush metal box/surface PVC box etc. comp. with nec. main lines for switch board from DB of mains of 2 nos. of 2.5 sq.mm wire and 1 no.of 1.0 sqmm pvc Insulated copper conductor wire laying in with 20 mm/25 mm dia PVC rigid conduits 1.5 mm thick ISI mark .These will be used with point wiring of light, fan, ex. fan, call bell points, etc { Max. 3 Switchboards in one circuit - One Sp MCB }.
a) | One 5A switch controlling one light/fan point | 25 | 600 | Nos | 15000
b) | One switch controlling Two light points | 10 | 650 | Nos | 6500
c) | 5A socket outlet with 5A switch ( on common board) | 1 | 300 | Nos | 300
2 | SITC of 20 A / 25 A , 230 V, with DP MCB all enclosed in a prefabricated M S boxes complete to the satisfaction of E.I.C. For SPLIT AC - CASSETTE AC 1.0 TR / 1.5TR / 2.0 TR unit with necessary require wiring from ACDB of 2 no of 4.0 sqmm wires and 1 no of 2.5 sqmm PVC Insulated copper conductor wire laying in with 20 mm/25 mm dia PVC rigid conduits 1.5 mm thick ISI mark. These will be used with point wiring of A.C. points ,etc . [This point should be installed near Split / window AC in concealed manner.] The height of switchboard must be at reachable point for easily operation. - from that point to Split AC , empty conduit + necessary bends must in concealed mode by ele. contractor. | 2 | 2500 | Nos. | 5000
B | SITC OF LIGHT/FAN FIXTURES:
Supply & Installation, testing and commissioning (including supply and fixing flexible wires from holder to fixtures hardwares etc.) of…. - The LED / PL / TUBE lamps should be of same make as fixture make. - The marking & cutting of fixtures should be in ele. contractor's scope.. fixtures should be approved by bank's ele. engineer / ele. consultant / architect. from the given make list before installations. LM 79 & LM 80 test reports to be submited. nichia LED / cree LED should be used by manufacture.
1 | LED 1 x 36 W ( 3000 lumens ) ( 2' X 2') RECESS MOUNTED LUMINAIRE with making earthing conection complete to be recessed in false ceiling with all necessary hardwares, hanging - die cast frame arrangement, chains, hook etc. complete. | 1 | 1950 | Nos. | 1950
3 | 1 x 9/10 W SQUARE/ROUND LED DOWN LIGHTER to be recessed in false ceiling with all necessary hardwares, chains, hook etc. complete. | 4 | 850 | Nos. | 3400
C | COMPUTER POWER SUPPLY SYSTEM:
1 | SITC of 2 nos. of 6 A, 5 pin Sockets and 1 no. of 6\16 A socket below table outlets with one 16 A switches Computer power supply with concealed company made metallic boxes or PVC flush box on walls / furniture's / trunking etc complete all respect with necessory wiring of mains of 2 no of 2.5 sq mm and 1 no of 1.5 sqmm pvc insulated copper conductor multi-stranded flexible wire with 20/25 dia. PVC conduits with accessories duly burried under floor with necessary chasing / breaking in floor and to be refinished with all necessary civil material etc. complete from DB to Computer power supply boards.{Maxi. 3 computers in one circuit}. complete with necessary termination etc. complete. LOOP POINTS MUST BE OF SAME SIZED WIRES. | 2 | 1300 | Nos | 2600
2 | S & I of 2 nos. of 16 A, 5 pin Sockets and 1 no. of with two 16 A switches row power supply with concealed company made metallic boxes or PVC flush box on walls / furniture's / trunking etc complete all respect with necessory wiring of mains of 2 no of 2.5 sq mm and 1 no of 1.5 sqmm pvc insulated copper conductor multi-stranded flexible wire with 20/25 dia. PVC conduits with accessories duly burried under floor with necessary chasing / breaking in floor and to be refinished with all necessary civil material etc. complete from DB to Computer power supply boards.{Maxi. 3 Raw Power Points in one circuit}. complete with necessary termination etc. complete. LOOP POINTS MUST BE OF SAME SIZED WIRES. | 2 | 1200 | Nos | 2400
D | DISTRIBUTION BOARD AND PANELS:
1 | SITC of metalic double door type distribution board with all necessary connection complete to be installed concealed in wall / surface mount complete. The DB should be of same make as MCB.
a) | 12-WAY SPN DB: (ATM LT & AC DB) | 1 | 8000 | Nos | 8000
incoming : 32A DP ELCB 100mA - 1 No.
Outgoing : 10 to 25 A SP MCB (4 nos) + AC Cyclic Timer - 1 No. for ATM AC
E | STRUCTURED CABLING:
1 | SITC of CAT 6, RJ 45 information outlet (I/O) of D-link make with front modular cover plate, flush box metallic or PVC for trucking system with terminations etc complete. SITC of CAT 6 UTP pvc insulated copper conductor data cable of D-Link make with 20/25 dia. PVC conduit with accessories duly burried under floor with necessary chasing/breaking in floor and to be regishide with all necessary civil material etc. or to be cleated on wall/ceiling witth saddles/spacer etc. necessary termination etc. with ferrule numbering at both ends of each of piece of cable etc. comp. | 2 | 1400 | Nos | 2800
2 | Supply & Fixing the Patch cord 2Mtr. Long (Factory built) When supplying, then first ask to BM/Consultant/Architect/Bank Authority. | 2 | 170 | Nos | 340
3 | Supply & Fixing the Patch cord 1Mtr. Long (Factory built) When supplying, then first ask to BM/Consultant/Architect/Bank Authority. | 2 | 150 | Nos | 300
|  | Total Rs. |  |  | 48590
| ROUNDED OFF TO |  | Rs. |  | 49000
For M/s Virat V. Thakore
PLACE : Ahmedabad
DATE : 08 - 11 - 2023 |  | ( VIRAT V. THAKORE )
Note: Yellow Mark Qty. Change as per your Drawing
Add 9W LED Down Light-3 No. outside Area in Drawing