## aBo
Date: 27.02.25
ABSTRACT OF COST FOR THE UCO BANK BRANCH + ATM
AT DARSHAN NAGAR ZO- AYODHYA
S.No. | DESCRIPTION | AMOUNT (Rs.)
1 | FURNISHING WORK
2 | ELECTRICAL |  | `
3 | AC WORK |  | `
TOTAL (Rs.)
Bharat and Associates.
Architects, Engineers, Interiors &
Landscape Designers,
Shop no-1,First Floor,Jeevan Plaza
Viram Khand-5 ,Gomti Nagar,Lucknow-226010
E-Mail: bharatandassociateslko@gmail.com
.

## Furn
PROJECT - BOQ FOR FURNISHING WORKS.
BANK - UCO BANK
AT DHARSHAN NAGAR BRANCH
*ALL ITEM TO EXCLUSIVE OF TAXES . Taxes to Mentioned By the Contractor.
*ALL WORKS TO BE DONE AS PER TENDER CONDITIONS.
Laminate use only-Century,Green,Sunmica (Other Laminate is not Acceptable)
S.NO. | DESCRIPTION OF ITEM | QUANTITY | UNIT | RATE | AMOUNT (Rs.)
A. | FURNISHING WORKS
1 | Toughened Glass
A. | Main Entrance Door For Branch + ATM | 150 | SQFT
Fully glazed Toughened Glass Single Leaf Door (1060mm x 2130mm): Providing and fixing in position fully glazed single leaf toughened glass door made out of 12 mm thk. clear toughened glass. The door shall be provided with heavy gauge patch fittings, floor spring, s.s. handle, special lock, etc. of approved make as per the requirement. The SS Handle to be of 22 mm dia and 300mm high. Work to be completed as per drawing and as directed by the Bank or its Architect.
B | Fixed Toughened Glass
| Fully glazed Toughened Glass Providing and fixing in position fully glazed single leaf toughened glassPartition made out of 12 mm thk. clear toughened glass. Work to be completed as per drawing and as directed by the Bank or its Architect. | 72 | SQFT
2 | FULL HEIGHT GLAZED & UNGLAZED PARTITION (HT -8'-6") | 290 | Sq.Ft |  |  |  | 35.25 | 299.625
Glazed Partition(upto false ceiling height only considered and above necessary ceiling supports to be provided) with Anodized Aluminium frame work, heavy sections (2mm thickness) of 2"x1.5" section, spacing of 2'0"x2'0" on bothsides and covered with 9mm thick BWR plywood finished with 1mm thick laminate of skriting & borders on both sides.Above 1'0"/2'6"/3'0" height partition,fixed with 8.0 mm bevelled glass with 3m sticker works door and teak wood beading with duco paint. Clear glass shall be finished with frosted film sticking over the glass of approved pattern and design. Rate to include providing cutouts and provisions to run electrical conduits, switches, etc..Cost include wastages, transports, loading, unloading charges, labours, materials, tools, lead, lift and etc.Complete as per drawings and instructions of the Architect.
The job shall also include for provision of laying conduits, switch boxes etc. The erection of partition shall include for expansion bolts cleats, clamps bolts, nuts, screws, rivets and other accessories, all complete up to the satisfaction of the Architect.
All door opening shall have rebated teak wood framework (size - 75mm x 50mm, as per profile) on vertical (2 Nos.) and horizontal (1 No.) sides, with melamine finish and rebate of 40mm x 12mm, all complete up to the satisfaction of the Architect.
the partition and doors shall have hinges floor springs/sliding arrangement/hydraulic door closer, mortise locks (Godrej make all), etc. The rate shall include cost of all materials, labour, T&P, wastages, etc. required for proper completion of work, all complete to the satisfaction of the Architect.
3 | Low Height Wooden Partitions (partly glazed) and Flap Doors
| Same specification as in 1 but P/F half height partition of height 4'-6" with wooden laminate till 3'-0" and 1'-6" height 12 mm thick glass secured with D brackets including all hardware necessary with the same specs.as above. | 55 | Sq.Ft |  |  |  | 8.75 | 39.375
3B | Ups parttion up to ceiling ht with biason board front side lemination | 120 | Sq.Ft
4 | CASH CABIN PARTITION(HT-7'-6"ONLY)
Decorative Grill (12mm thk)-hexagonal opening as per instruction of Bank's Engineer/Architect.) AII exposed edges of Plywood shall be fixed with 1/8" C.P.Teak Lipping.
Providing and fixing of Cash Enclosures at height of 7'-4" with Anodized aluminium frame work, heavy sections (2mm thickness) of 2"x1.5", spacing of 2'0"x2'0" on bothsides and covered 6mm thick BWR plywood finished with 1mm thick laminate of (As per bank colours) for skriting & borders.Partition shall have provision for opening and 19mm BWR plywood tray for challan receiving purpose. Cost include aluminium grill and fixed with teak wood beading and duco paint. Cost also include 3 Nos of Solid core flush Doors with sizes of 2'6"x7'0", fixed in the partition. Door shall have teak wood beading and lipping with duco paint. Door finished with 1mm thick laminate of (As per bank colours) for base and (As per bank colours) for skirting of approved pattern. Door shall have 8mm glass fixed with teak wood beading and duco paint. Rate to include hardware's like brass hinges, godrej three nos of night latch, door closure, door stopper and handles. Cost also include cash transaction opening shall be provided with door arrangements made with BWR plywood frame work finished by laminate, duco paint and locking system. Cost include wastages, transports, loading, unloading charges, labours, materials, tools, lead, lift and etc.Complete as per drawings and instructions of the Architect.
| Solid till 4’-0’’ then Aluminium Decorative Grill height till 7’-0”then again solid | 100 | Sq.Ft |  |  | 350
5 | Glass Barrier on cash cabin and front glass for counter (12 MM NECESSARY) | 45 | Sq.Ft
Providing and fixing glass barrier (as per profile and design) in front of cash and ledger counter made out of 12mm thick polished edged float glass (Make – Modi guard or equivalent). It shall have 25mm x 20mm teakwood beading (as/shape approved by the Architect) to hold the glass from sides and top (optional). All teak wood surfaces shall be melamine polished. The rates shall include for cutting (in geometrical shape) and polishing the edges, all complete to the satisfaction of the Architect.
6 | Computerised Ledger & Cash Counter
Providing and placing in position ledger counter with top, vertical sides/dividers, skirting and fascia made out of 19mm thick water proof board with 1mm thick laminate (as/shade approved by the Architect) on all exposed surfaces. It shall also have 75mm x 40mm teak wood runners below the top and for footrest below. Every unit shall be provided with a side unit (size - W-500mm, H-750mm, D-500mm approx.), consisting of 150 mm deep drawer at top and a cabinet with open able/hinged shutter below.
. The fascia of drawer and shutter of cabinet below shall be made out 19mm thick water proof board with 1mm thick laminate (as/shade approved by the Architect) and sides and bottom/internal surface of drawer shall be made out of 12mm thick water proof ply. The side unit shall have CAM locks, handles, guides, sliding units, hinges, magnetic catcher’s etc. of approved make. Every unit shall be provided with a keyboard drawer unit (size - W-550mm, H-100mm, D-300mm approx.) below. The counter shall have 100mm deep fascia, below the top, in which keyboard drawer unit shall be adjusted.
It shall be made out 19mm thick water proof board with 1mm thick laminate (as/shade approved by the Architect) and sides and bottom of drawer shall be made out of 12mm thick water proof ply. The unit shall have CAM locks, handles, guides, sliding units etc. of approved make. The job shall include for 6mm x 6mm grooves in between sides and open able drawers and hinged shutters. All the exposed edges of water proof board and ply shall be provided with 6mm thick teak wood/hard wood lipping. All teak wood surfaces shall be 1mm thick laminate , all internal & rear surfaces shall be laminated with 1.00 mm thick laminates (paint not to be done).
a | High Level | 5 | Rg.Ft
High level (two levels) Computerised cash counter.
Lower level top shall be 900mm wide and at 750mm level from floor & upper level top shall be 250mm wide (and at 1150 mm level from floor
b | Low Level | 9 | Rg.Ft
Low level (two levels) Computerised ledger counter.
Lower level top shall be 900mm wide and at 750mm level from floor & upper level top shall be 150mm wide and at 900mm level from floor
7 | Tables
A | Manager's Table with Side credenza include the 12 mm thick glass | 1 | No.
Providing and placing in position tables with top, vertical sides/dividers, skirting and modesty panel made out of 19mm thick water proof board with 1mm thick laminate (as/shade approved by the Architect) on all exposed surfaces. It shall also have 75mm x 40mm teak wood runners below the top and for footrest below.Every table shall be provided with a side unit (size - W-500mm, H-750mm, D-500mm approx.), consisting of 150 mm deep drawer at top and a cabinet with open able/hinged shutter below.
The facia of drawer and shutter of cabinet below shall be made out 19mm thick water proof board with 1mm thick laminate (as/shade approved by the Architect) and sides and bottom/internal of drawer shall be made out of 12mm thick water proof ply. The side unit shall have CAM locks, handles, guides, sliding units, hinges, magnetic catcher’s etc. of approved make. Every table shall be provided with a keyboard drawer unit (size - W-550mm, H-100mm, D-300mm approx.) below. The table shall have 100mm deep facia, below the top, in which keyboard drawer unit shall be adjusted. It shall be made out 19mm thick water proof board with 1mm thick laminate (as/shade approved by the Architect) and sides and bottom/internal surface of drawer shall be made out of 12mm thick water proof ply. The unit shall have CAM locks, handles, guides, sliding units etc. of approved make.
The job shall include for 6mm x 6mm grooves in between sides and open able drawers and hinged shutters. All the exposed edges of water proof board and ply shall be provided with 6mm thick teak wood/hard wood lipping. All teak wood surfaces shall be melamine polished and all internal & rear surfaces shall be laminated with 1.00 mm thick laminates (paint not to be done). Every table top shall be provided with 10 mm thick float glass (as per profile) with polished and beveled (25mm wide) edges all complete to the satisfaction of the Architect.
B | Officer Table size 4'-6"x 2'-6"x 2'-6" With Out Side Table include the 12 mm thick glass | 1 | No.
SPECIFICATION AS PER MANAGER TABLE( PART -A)
8 | Writing Table & Brochure Holder | 1 | No.
Providing and fixing in position (with rear wall) slip and customer writing desk (as per design) of over all size - 1200mm x 450mm x 300mm. The fixing shall include for expansion bolts, cleats, clamps, bolts, nuts, screws, rivets and other anodized accessories, all complete up to the satisfaction of the Architect.
.The writing top and facia/sides shall be made out of 19mm thick water proof board with 1mm thick laminate (as per shade approved by the architect), on all sides and . It shall be laid over the base of 19mm thick water proof board (already considered in various items.) and fixed with araldite. It shall include for beveling and polishing at all the exposed edges. The rate shall include cost of all materials, labour, scaffolding, wastages, polishing and T& P etc. It shall be made out of 12mm thick water proof plywood (two surfaces of 6mm thickness, fixed together, where required) on rear and both sides.
The front shall be made out of 12mm thick glass (as per profile). It shall be fixed in the grooves, made in side members, in an inclined manner (as per profile in drawing enclosed) with a gap of 75mm (max.) in between. The space shall be further divided in four equal parts with help of 12mm thick water proof plywood. All edges of the glass shall be polished.All the exposed edges of water proof board and plywood shall be provided with 6mm thick teak wood/hard wood lipping. All teak wood surfaces shall be melamine polished and other internal surfaces shall be painted with two coats of synthetic enamel over one coat of primer, all complete to the satisfaction of the Architect
9 | Complaint & Suggestion Box & CHEQUE DROP BOX | 2 | No.
Providing and fixing in position complaints/suggestion box (as per design) with hinged shutter of size - 450mm x 600mm x 150mm made out of 19mm thick water proof board with 1mm thick laminate (as per shade approved by the architect) on all exposed surfaces. It shall have 6mm thick water proof plywood on the back.
.The hinged shutter shall be made out of teakwood (section - 25mm x 50mm) framework, with 4mm thick float glass, fixed with teakwood (size - 12mm x 12mm) beading. The unit shall have cam locks, handles, spring hinges, magnetic catchers etc. of approved make. All the exposed edges of water proof board or ply shall be provided with 6mm thick teak wood/hard wood lipping. All teak wood surfaces shall be melamine polished and other internal surfaces shall be painted with two coats of synthetic enamel over one coat of primer, all complete to the satisfaction of the Architect.
10 | Notice Board | 1 | No.
Providing and fixing in position notice board (as per design) of size - 900mm x 600mm x 150mm. The sides shall be made out of 19mm thick water proof board with 1mm thick laminate (as per shade approved by the architect) on all exposed surfaces.It shall have 12mm thick tack The front shall have 6mm thick float glass sliding shutter in two parts.
It shall also have 19mm wide two track aluminium channel for sliding arrangement, all around, along with locking arrangement.board (Make – Cellotex or equivalent) wrapped with stretched blazer cloth (Make- Raymonds), of Rs. 200.00 per Mt. (approx.) in colour and pattern approved by the Architect. It shall be fixed with help of kail/partal wood (sect. 19mm x 25mm) frame work. It shall be covered with 6mm thick water proof plywood, on the back. All the exposed edges of water proof board and ply shall be provided with 6mm thick teak wood/hard wood lipping. All teak wood surfaces shall be melamine polished and other internal surfaces shall be painted with two coats of synthetic enamel over one coat of primer, all complete to the satisfaction of the Architect.
11 | False Ceiling(Armstrong) | 483 | Sq.Ft.
Providing and fixing in position false ceiling in armstrong 600 x 600 x 15 /16 mm dune supreme RH 99 prima tile with regular edge frame work as specified by armstrngcompany with suspenders making necessary frame work for A.C. Ducting for diffusers and light fitting.
12 | False Ceiling Works (Gypsum) with cove design & CNC CUTTING JALI & MDF JALI
| Providing & fixing with necessary scaffolding frame in 22 gauge GI channel /angle, placed at appropriate grid, fixed to RCC slab, beam, wall etc. with fasteners /screws finished with 12.0mm Gypsum sheets joints covered with POP slurry/tape. Rates shall include painting (One Coat of putty, one coat of primer coat and two coats of acryilc paint). Rates shall include providing necessary cut-outs & additional support frames for electrical fixtures, A.C. grills, vertical drop upto 1'6" etc | 322 | Sqft
13 | Column & Wall Panelling (As per Direction BY Architect ) | 210 | Sqft
| Providing & fixing in position 2"x2" kailwood frame and finished with 6 mm thk. Commercial ply on both sides with1.0 mm thk. Laminate on top as per instruction of the Architect |  |  |  |  | 9
14 | Designer MDF board column cladding with CNC Cutting and backing of Acryllic /Metalim, Jaali to be painted in white duco mpaint and LED strip lighting to be included in this rate.The support system to be as above. | 110 | Sq.Ft.
15 | Acrylic Emulsion with POP Base. | 3496 | Sq.Ft.
Painting on undecorated / decorated wall and ceiling surfaces with two or more coats of acrylic emulsion(Asian/ Berger make) (as / shade approved by the Architect) of approved brand. It shall include for preparing the surfaces clean, even and smooth with thoroughly brushing with broom, scratching with patti and sand papering respectively, so that the surfaces are free from oil, grease, dirt, mortar droppings & other foreign and loose matter. It shall also include for preparing the surface and filling of holes with plaster of paris before priming coat of whiting / approved primer. this work is included Front Elevation painting (including First Floor elevation painting )Complete in all Respects .
The rate shall include cost of all materials such as plaster of paris, whiting /primer, glue (Fevicol), indigo / stainer, brushes, sand paper, patti, dhoti, broom stick, clean water with storage and other containers, labour, scaffolding / ladder charges, cleaning of floors and other sundries etc., all complete to the satisfaction of the Architect.
16 | Low /full height Storage Racks | 150 | sqft
S1-Storage (Low Height)
Size- 6' Length X 2'-6" highX 1'-4"deep
Ply Wood-19.0mm thick for side top and door & back 6.0mm with shutters, shelf 19.0mm
Shelf-19.0mm thick Ply
Handle-Brush finish stainless steel
Lock-Vijayan/Godrej
| all internal & rear surfaces shall be laminated with 1.00 mm thick laminates (paint not to be done). | 220 | sqft
17 | ACP PANNELING (As per Bank colour) | 179 | sqft
Rolling Shutter Box.
Frame Work-2" X 2" X 1.5 mm thick Aluminium Tubular section (Horizontal/Vertical) Jindal /Alstrong Make
Aluminium Composite Panel-3.0mm thick of approved colour with bonding material
18 | Main Panel Boxing | 42 | Sqft
Providing & fixing in position 2"x2" kailwood frame and finished with 6 mm thk. ply on Outer sides with1.0 mm thk & Inner Side of Storage Paste 1.5 Thick Aluminium Tubular Section of Approved Colour Pattern . Front Side of Storage Aluminum Jali for Ventilation of the Panel & the Measurement of the Storage only front Facia of the Storage (Lenth x Height ) . Alll work Complete to the Satisfaction of the Bank /Architect .
19 | Wooden Planter with Plants
| Providing and placing in position planter made of phenol bonded 19 mm thick commercial board with top front and sides finished in 1.0 MM Thick laminate including GI trough with sand and marble chips filling and artificial plants as per the approval of the architect of not less than Rs.750. The design of the grooves shall be as per detailed drawing and complete as per Architects direction | 0 | No
20 | Synthetic Enamel | 779 | Sqft
• Surface preparation.
• Rub with sand paper to ensure that the surface is dry and free from abrasions, dust, dirt, grease etc.
• Fill the holes etc. in the wood, if any with putty.
• Let the surface dry before application of paint.
How to apply
• Generally two coats of synthetic enamel finishes are required for satisfactory results.
• After priming the surface with two coats of wood primer white and one coat of putty apply first coat of paint and finish as recommended.
• Allow a minimum time gap of 8 hrs in between two coats.
• First coat should be sanded with emery paper grade 320/400 and wipe clean before application of subsequent coats.
• For make and shade please refer to the schedule of interiors, furniture & finishes.
21 | Fire Extinguisher Rack | 1 | No
22 | P&F vertical Venetion blinds made out of 100mm wide strips as/ shade approved including supports, | 45 | Sqft
23 | post construciton antitermite treatment | 0 | Sqft
by drilling holes and injecting chemical as per
IS code from a reputed company with
10 years warranty certificate
24 | Sofa (Three SEATER) | 2 | Nos
| e. PU molded three seater waiting seats upholstered with upholstery of about Rs.400/- per m. (as per approval of the architect) with 50mm thick 32 density U foam.The whole structure fabricated on tubular frame powder coated upto 95 microns Inclusive of all materials, labour, T&P taxes etc. completed to the satisfaction of architect. | copy
25 | Center Table with glass Size : 4'-0''x2'-0'' | 1 | Nos
| Total |  |  | Total
GST Extra
Sl. No. | Materials | Approved manufacturers / suppliers
1 | Paint | I.C.I. ( Dulex - Duco) / Asian paints / Goodlac Nerolac
2 | Plywood | BWR- Century/Green/Archid/ only Premium quality
3 | Wood preservative | BWR- Century/Green /Archid/ only Premium quality
4 | False ceiling | Armstrong , Indian gypsum board
5 | Laminates | Sunmica/ Archid/Century/Green/ 1mm thick as per bank approved color
6 | Screws | G.K.W./Nettle fold
7 | Adhesive | Fevicol SH
8 | Night latch | Godrej
9 | Locks | Godrej
10 | Aluminium door frame | Jindal
11 | Glass | Modi/Asahi/Saint Gobain
12 | Aluminium cladding | Eurobond/Altobond/Alukbond
13 | Key board drawer | EBCO
14 | Telescopic CPU stand | EBCO
15 | Cable organiser ( wire manager) | EBCO
16 | Vitrified tiles | Jhonsions Perlto
17 | Venetion blind | Vista, Luxaflex
Bharat & Associates
Bharat and Associates.
Architects, Engineers, Interiors &
Landscape Designers,
Shop no-1,First Floor,Jeevan Plaza
Viram Khand-5 ,Gomti Nagar,Lucknow-226010
E-Mail: bharatandassociateslko@gmail.com
.

## Elec.
PROJECT - BOQ FOR ELECTRICAL
BANK - UCO BANK
BRANCH+ ATM -DARSHAN NAGAR ZO- AYODHYA
S.NO. | PARTICULARS | Unit | Qty | Rate | Amount
A -Electrical wiring (All switches to be Modular type - Anchor/ Havells or equivalent approved by architect)
Light & Fan points
1 | Supply & Installation of concealed point wiring using 600v grade 3x1.5 Sq.mm copper conductor PVC insulated wires (with proper R,Y,B color code ) pulled through heavy gauge 19mm PVC conduit pipe heavy duty concealed in wall/ floor/ panelling/ partitions or above false ceiling as per requirement including 2 Nos. 2.5 sqmm circuit wires from the relevant DB and also including 1.5 sqmm green color copper earth wire and switch plate, switches, etc. as approved by the Bank's Engineer/Architect. All switch & sokets shall be modular type complete with cover plate & GI/ MS box. The work shall also include for cutting chase for conduits and moulded boxes, if required, in the wall/ floor (Without damaging the building/wall) along with clamping the conduit at every 600mm interval & finally finishing the surface & matching the same with the existing surface.The rate should include the cost of all materials, labour, T&P, taxes & levies, scaffolding, shifting of furniture, carting away the debris and cleaning the floor etc.The job shall be complete & to the entire satisfaction of the Bank.
a | Light points + AFF points including the cost of 6A switch | Point | 41
b | Ceiling Fan Point including the cost of 6A Switch along with electronic regulator | Point | 1
c | Wall Fan Point along with 6A switch | Point | 8
d | 6A switch & Socket on SDb | Point | 10
2 | RAW POWER POINT
| Single Power Points - Supply & Installation of point wiring for Raw power plug points on workstations / table for computers using 2 X2.5 + 1x1.5 Sq.mm copper conductor PVC sheathed flexible wire pulled through heavy gauge 19mm PVC conduit pipe heavy duty concealed in wall/ floor/ panelling/ partitions or above false ceiling as per requirement. Each point consisting of 1 nos of 16A , 2/3/5 pin sockets & 1 No.16A Switch wired together forming one point. The earth wire of green color only. All switch & sokets shall be modular type complete with cover plate & GI/ MS box. The work shall also include for cutting chase for conduits and moulded boxes, if required, in the wall/ floor (Without damaging the building/wall) along with clamping the conduit at every 600mm interval & finally finishing the surface & matching the same with the existing surface.The rate should include the cost of all materials, labour, T&P, taxes & levies, scaffolding, shifting of furniture, carting away the debris and cleaning the floor etc.The job shall be complete & to the entire satisfaction of the Bank. | Point | 10
3 | AIR CONDITIONING
1 | AIR CONDITION POINTS - Circuit wiring with 2x4.0sq.mm + 1x 1.5sq.mm stranded Cu. conductor (Finolex/Anchor/Skytone) in 19mm M S conduit pipe heavy duty 16swg laid & concealed in wall/ floor/ panelling/ partitions or above false ceiling as per requirement. The job includes supply & fixing of flush mounted 4in one appliance protector pre-wired, IP 20 with factory fitted 25A, 2P MCB and 25A socket (Hagers/ Siemens/ ABB). The rate should include the cost of all materials, labour, T&P, taxes & levies, scaffolding, shifting of furniture, carting away the debris and cleaning the floor etc.The job shall be complete & to the entire satisfaction of the Bank. | Point | 7
4 | UPS
A | Sub Main Wiring/ Cabling - : SITC of sub main wiring 4nos. 10 sq.mm Stranded copper wires for UPS Input from main incoming panel to incoming Db of UPS power input system etc. in 25mm dia PVC haevy duty conduit complete to the satisfaction of the bank. | JOB | 1
B | UPS Power Input System: SITC of 4way TPN Double door Db IP 42 horizontal Complete with 1no. Incoming 32A. TP MCB and 3 x 32A 2P MCB's to regulate supply for UPS complete in all respect as required and to the satisfaction of the bank. | Set | 1
C | Wiring for UPS Input & UPS Output (For both Critical 2Kva & Non- Critical 3Kva UPS) with 2x4.0sq.mm + 1x 1.5sq.mm stranded Cu. conductor (Finolex /Anchor /Skytone) to be laid in 19mm PVC pipe heavy duty/ Flexible pipe laid & concealed in wall/ floor/ panelling/ partitions or above false ceiling as per requirement. The rate should include the cost of all materials, labour, T&P, taxes & levies, scaffolding, shifting of furniture, carting away the debris and cleaning the floor etc.The job shall be complete & to the entire satisfaction of the Bank. | JOB | 1
D | S/F of 32A 2P MCB in 2way metallic box including proper connectionbs thru lugs. Both the Db's shall be inter looped- Qty included in item 3. (2nos. For ATM and 2nos. For Branch) | Each | 1
E | UPS Output Power Distribution System: SITC of 12 way SPN Db Double door IP -43 Siemens make with 32A DP 10kA MCB and 09 nos. SP 10kA MCB complete in all respect and as required & to the satisfaction of the bank. Siemens/ L&T/ MDS/ Schnider | Set | 1
F | Input Wiring for UPS Db's with 2x4.0sq.mm + 1x 1.5sq.mm stranded Cu. conductor (Finolex /Anchor /Skytone) to be laid in 19mm PVC pipe heavy duty/ Flexible pipe laid & concealed in wall/ floor/ panelling/ partitions or above false ceiling as per requirement. The rate should include the cost of all materials, labour, T&P, taxes & levies, scaffolding, shifting of furniture, carting away the debris and cleaning the floor etc.The job shall be complete & to the entire satisfaction of the Bank. | JOB | 1
G | Supply & fixing of 4nos. 6A switches & sockets (Modular type c/w MS/GI box & cover plate) complete with computer point circuit wiring with 2x2.5sq.mm + 1x 1sq.mm stranded Cu. Single core Copper conductor (Finolex/Anchor/RPG) to be laid in PVC conduit 1" dia/ vertical drops heavy duty laid & concealed in wall/ floor/ panelling/ partitions or above false ceiling as per requirement. | Per Node | 10
5 | MAIN INCOMING PANEL & DISTRIBUTION
A | SITC of 100A Kit kats fuse unit 3nos in wooden patra complete with 100Amp. Neutral link complete in all respect as required. | Set | 1
1 No for Metre
1 no for Panel to Outer Side Of Wall (For Generator Connection)
B | Main Incoming Panel
| Supply, Installation, Testing & Commissioning of main distribution board panel fabricated of 18swg (powder coated) comprising of | Nos. | 1
Indicator lamps 3 nos.
Voltmeter & ammeter(one each)
Rotary selector switches 2 nos for voltmeter & ammeter
Busbar (each of RYB +N) copper 100 amp each
125 Amp MCCB(Siemens/ L&T/ ABB/ Schnider) incoming 3P adjustable 25kA
Changeover TPN 100 amp for DG set (Havells/ ABB/ Sochomac)
Outgoing 63A 3P MCB`s - 6 nos.
Outgoing 32Amp 2P MCB's - 6 nos.
Earth bus bar 25x5mm GI strip - 2nos. At the bottom.
6 | Supply Installation testing & commissioning of XLPE insulated Armoured Al.codutctor cable between main panel & DB`s & generator of required thickness of approved make Skytone/ Havells based on the load assessment & confirmation of the same with architect. This rates include cost of lugs at both the ends
| 3.5 x50 sq.mm cable from Meter to Kit kat to the main panel & Pole (Aprrox - 20 mtr ) | JOB | 1
| 4c x20 sq.mm cable from Main Panel TO LHS DB (Aprrox - 20 mtr) | JOB | 1
| 4c x 20 sq.mm cable from Main Panel to RHS DB (Aprrox - 20 mtr) | JOB | 1
| 4c x 20 sq.mm cable from Main Panel to Kikat (Generator) ( Aprrox - 40 mtr) | JOB | 1
7 | Supply, installtion, testing & commissioning of VTPN Db double door with MCB as incomer IP 42 complete in all respects for AC, PP and L & F as under - Siemens/ Hager/ Lagrand/ ABB
A | RHS 6way VTPN db - Loaction RHS wall opposite Cash cabins (From entrance to Rear record room & Toilet area) - Siemens 8GB0406VRC or equivalent
| Incomer - 63A 3P MCB 10kA adjustable neutral to be directly connected to neutral bus | Each | 1
3no. 32A 1P-MCBs 10 KA - AC's - 2nos. RHS & 1rear
3no. 16A 1P-MCBs 10 KA - for single power points - 2 cash & 1 May I help You & 2nos. D/W
4nos. 10A 1P-MCBs 10 KA for L&F
4os. 6A 1P-MCBs 10 KA for L&F
Blanking Plates - 2no.
All connections to be terminated thru lugs
B | LHS 6way VTPN db - Loaction LHS wall behidn advance (From LHS LV Cash to Mgr Rm)- Siemens 8GB0406VRC or equivalent
| Incomer - 63A 3P MCB 10kA adjustable neutral to be directly connected to neutral bus | Each | 1
4o. 32A 1P-MCBs 10 KA - AC's - 3nos. LHS & 1 Mgr Rm
4no. 16A 1P-MCBs 10 KA - for single power points - ( LV cash, 2 CRE, 1Advance, 2 MR & 2 Router)
2nos. 10A 1P-MCBs 10 KA for L&F
2os. 6A 1P-MCBs 10 KA for L&F
Blanking Plates - 2no.
All connections to be terminated thru lugs
8 | Glow sign Board - Circuit wiring with 2x2.5sq.mm + 1x 1.0sq.mm stranded Cu. conductor (Finolex/Anchor/Skytone) to be laid in 19 mm PVC pipe heavy duty laid & concealed in wall/ floor/ panelling/ partitions or above false ceiling as per requirement. The rates should include the cost of all materials, labour, T&P, taxes & levies, scaffolding, shifting of furniture, carting away the debris and cleaning the floor etc.The job shall be complete & to the entire satisfaction of the Bank. | JOB | 1
E -EARTHING
9 | For Main Panel - S/burying of Dual pipe technology (Pipe in Pipe) earthing electrode having GI 80mm O/D pipe with 25 micron coating, 3metres long. The space between two pipes to be filled with Highly conducive & Non corrosive chemical compound. The installation shall be thru earth auger. The vacant space between pipe & hole shall also be filled with compound all around. The job also includes S/F of GI strip clamp with two holes (with SS/GI bolts & nuts) on the electrode & taking two earthing leads of 25 x 5 mm GI strip (Assumed length of 10m - beyond 10m to be paid extra) upto Main panel complete in all respects with guaranteed E/N voltage of less than 3 volts and resistance less than 1 ohms. The distance between two earthing pits to be 10ft or more INCLUDING Earth wire 4 sq mm copper wire . Approx -80 mtr (2 FOR BRANCH & 1 ATM ) | Per Icn. | 2
10 | F - FIXTURES & FITTINGS
A | a) Supplying and fixing Philips make 36W LED FLAT PANEL after disconnection of existing fitting 2'x2' size in grid type false ceiling, 600x600 suitable for recess mounting,CRCA sheet, asthetic looking, or eqv Philips/havells | Each | 10
B | b) Supplying and fixing Philips make or eqv 10 W LED round type downlighter (Philips/ wipro /Jaguar) | Each | 24
C | Supply installation testing and commissioning of 1*20watt Batten type tubular LED light fitting with LEDs, driver, diffuser, and housing complete in all respects in UPS room and record /wc/bath room /suitable place with complete in all respect with required color on need basis. | Each | 5
D | S/F of angle holder for bulbs including cost of 11w CFL lamp for Toilets | Each | 2
E | i) Supply & installation of wall bracket fan 450 MM METAL BODY (Heavy duty/ high speed) Make Bajaj/cropmton greaves/havells/Orient (to be supplied after consultation with architect/Electrical Engineer as per approved drawing) | Each | 8
F | g) Supply & fixing of the 1200 mm 48") Sweep Ceiling fan (Orient PSPO/crompton greaves/havells) with downward rod(below false ceiling), canopy etc. including of PVC flexible copper wire.(white colour)( High speed) (Warranty Cerificate is necessary)with downward rod, circular boxes, ball sockets, ceiling plates,suitable arm bracket etc. including connection with wire)White colour (WITH REGULATOR) | Each | 1
G | Supply & Fixing of fresh air fan 12" - Crompton Greaves/ Usha/ Khaitan/ Bajaj | Each | 3
H | e) Supplying and fixing LED strip 3000 K 24 watt 5 mtr length with driver (Philips or Havells or Cormpton ) | SET | 5
11 | H - TELEPHONE
A | P/f Krone or equivalent box in the server room & out side of the Branch with a ten pair connecting strip for telephone with lock & key | Each | 2
B | 10 Pair Cable with Connection from main Panel to entrance of the Branch | JOB | 1
C | Supply & fixing on wall/ furniture/ partition recessed type non modular telephone socket outlet (RJ-11) with mounting box & front plate complete with chase cutting, mending good etc. as required complete with Supply & laying of 2pair 0.61mm dia. PVC insulated telephone cables through 19mm dia rigid PVC conduit of suitable diameter as directed by the consultant from telephone junction box to telephone socket outlet including interconnection mending good etc. as required complete in all respects. | Each | 4
D | Wireless Call Bell of Approved Quality (Orient,Sunshine) | No. | 1
12 | I - DATA CABLING
A | Supply & Fixing of XL RJ 45 toolless information outlet with Duplex face plate with dual connectors Grey colour cat 6e including cost of supplying & laying CAT 6e (as directed by Architect from Server to Switch, Switch to computer I/O data socket as required complete in all respects) in 25mm dia rigid PVC conduit (including laying of GI draw wire complete with junction box, circular box, elbows, bends & other accessories as required by chase cutting on floor, wall, through partition or over false ceiling.The data cabling pipe should be laid at a minimum distance of 3ft from pipes laid down for power distribution) including interconnection with connectors as required complete in all respects. | Each | 10
B | Supply & fixing of 7ft Grey colour Patch chord Giga speed Systimax/ D link make | Each | 10
C | Supply & fixing of 3ft Grey colour Patch chord Giga speed Systimax/ D link make | Each | 10
D | S/F of 24Port Jack Panel fully loaded systimex make | Each | 1
E | S/F of 9 U wall mounted rack c/w fan etc as required | Each | 1
F | S/F of Cable Manager as required | Each | 2
Total
GRAND TOTAL AMOUNT (gst extra)
List of approved materials
| Materials | Approved manufacturers/suppliers
1 | MCCB | MDS legrands, ABB, GE, SIEMENS
2 | Changeover | Indo Asian/ HPL Socomec / GE/ Standard stangaurd
3 | Distribution board | MDS / Standard / Indo Asian / HPL
4 | MCB | MDS / Standard / Indo Asian / HPL
5 | Cable | Gloster / Rallison / Incab / CCI
6 | Copper wire | Finolex/anchor
7 | Switch / Socket / Call bell and accessories | Anchor / Havells / CPL / MDS / Philips
8 | Electrical Light Fittings / Fixtures Complete | Philips
9 | Wall Fan / Ceiling Fan / Exhaust Fan | Khaitan/Havells
Bharat and Associates.
Architects, Engineers, Interiors &
Landscape Designers,
Shop no-1,First Floor,Jeevan Plaza
Viram Khand-5 ,Gomti Nagar,Lucknow-226010
E-Mail: bharatansassociateslko@gmail.com
.

## ac
Ref No.: BA/02/2025 |  |  |  | Dated : 27.02.25
DETAILED BOQ / SPECIFICATION FOR BILL OF QUANTITIES
OF AC WORK FOR UCO BANK BRANCH + ATM AT DARSHAN NAGAR ZO- AYODHYA
S. No. | DESCRIPTION | QUNTITY. | UNIT | RATE | AMOUNT
1 | Suppy, Fixing, Testing & comissioning of following star rated AC units, with evaporator copper coil & imported refrigerant joints, with wireless remote controller (Make:- Bluestar / Voltas / Carrier)
(i) | Cassette 2 TONE - INVERTER TECHNOLOGY | 0 | No.
2 | S.I.T.C. of 3 Star 1.5 Ton capacity High wall mounted Split A.C. comprising Indoor & Out-door units. Indoor unit comprising Multi Row DX cooling coil, expansion valve, drier, motor driven air-blower with metallic frame etc. Out-door unit will have rotory/scroll compressor, condenser coil, & fan, Cordless remote control unit etc. including refrigerant gas charging. | 5 | No.
3 | S.I.T.C. of 3 Star AC as per specifications given in item no 3 above But For 1.0T Split A.C.'s | 2 | No.
3 | SITC of interconnecting refrigerant pipe work with closed cell elastomeric nitrile rubber tublar in sulation between each set of indoor & outdoor units as per specification, all piping inside the room shall be peoperly supported with MS hanger & clamps including cabling from indoor to outdoor unit.
(i) | Refrigerant Pipe for 2 TONE AC - INVETER (Cassette) | 0 | Rmt
(ii) | Split 2.0/1.5/1.0 TONE - INVERTER | 62 | Rmt
4 | Providing & fixing, testing and commissioning of wall mounted copper wound voltage stabilizer suitable for split all accessories. Input Voltage range : 140-280 V, Output : 230 V (Make:- LIVEGAURD/ Blue- Birds & Reputed Firm .)
(i) | CAPACITY: 5 KVA | 0 | Nos
(ii) | CAPACITY: 4 KVA | 7 | Nos
5 | SITC of rigid CPVC piping complete with fittings supports as per specification tions & duly insulated with 6mm thick closed cell nitrile rubber insulation.
(i) | Drain Pipe for 2.0 Tone AC (Cassette) | 0 | Rmt
(ii) | Drain Pipe for Split 2.0/1.5 TR (Split) | 57 | Rmt
6 | Supplying and laying of Extra Electrical interconnecting control cable from indoor to outdoor of size as specified by the manufacturer suitable for 1.0/ 1.5 / 2.0 TR Split type AC. | 62 | Mtr
7 | M.S. stand with monkey cage - [ In door & out door units | 7 | No
8 | Installation Charges . | 7 | No
9 | Autometic Timer Switch in ATM | 1 | No
Total
Note : GST will be extra.
Bharat and Associates.
Architects, Engineers, Interiors &
Landscape Designers,
Shop no-1,First Floor,Jeevan Plaza
Viram Khand-5 ,Gomti Nagar,Lucknow-226010
E-Mail: bharatandassociateslko@gmail.com
.